## Cover Page (metadata)
Site Name | Sample Solar, LLC
Site Address | 1234 First St. Anywhere, NC 12345
Queue Number | CHKLIST-00000
IPP Number (when applicable) | 123abc
Maximum Physical Export Capability | 4.975 MW
Interconnection Voltage | 22.86 kV
Commenced Operation Date | 2015-12-21
Last Commissioning Test Date | None conducted
Date of last specified settings (SS) update
Date of last applied settings (AS) verification | 2021-06-14
Version History

## Inverter Settings
Parameter Description | Specified Settings |  | Applied Settings
| DEP/DEC Default | Units | Value | Units
OV2, overvoltage must trip magnitude per unit value | 1.2 | V p.u. |  | V p.u.
OV2, overvoltage must trip duration | 0.167 | s |  | s
OV1, overvoltage must trip magnitude per unit value | 1.15 | V p.u. |  | V p.u.
OV1, overvoltage must trip duration | 2 | s |  | s
UV1, undervoltage must trip magnitude per unit value | 0.88 | V p.u. |  | V p.u.
UV1, undervoltage must trip duration | 2.25 | s |  | s
UV2, undervoltage must trip magnitude per unit value | 0.5 | V p.u. |  | V p.u.
UV2, undervoltage must trip duration | 1 | s |  | s
OF2, over-frequency must trip magnitude | 62 | Hz |  | Hz
OF2 , over-frequency must trip duration | 1 | s |  | s
OF1, over-frequency must trip magnitude1 | 61.4 | Hz |  | Hz
OF1 , over-frequency must trip duration1 | 300 | s |  | s
UF1, under-frequency must trip magnitude1 | 57.8 | Hz |  | Hz
UF1, under-frequency must trip duration1 | 302 | s |  | s
UF2, under-frequency must trip magnitude | 56.8 | Hz |  | Hz
UF2, under-frequency must trip duration | 1 | s |  | s
Constant power factor setpoint (1.0 is unity power factor) | 1
Constant power factor excitation setting (injecting or absorbing) | Unity | Text |  | Text
Configured maximum active power output (Pmax) | Reference to IA | kW |  | kW
Minimum intentional restart delay | 300 | s |  | s
Momentary cessation low voltage per unit value2 | 0.5 | V p.u. |  | V p.u.
Momentary cessation high voltage per unit value2 | 1.2 | V p.u. |  | V p.u.
Notes:
1. Shown here are the UL 1741-SA values from page 8 of the Duke Energy DER Voltage & Frequency Document. If inverters feature only one level each of user-editable over/under frequency protection, ensure that they are set to 62.0 Hz at 1.0 sec and 56.8 Hz at 1 sec, as shown on page 9 of the Duke Energy DER Voltage & Frequency Document.
2. Momentary cessation may not be available on all inverters, may be omitted if not a valid parameter.

## Recloser or Relay Settings
Parameter Description | Specified Settings |  | Applied Settings
| DEP/DEC Default | Units | Value | Units
OV2, overvoltage must trip magnitude per unit value | 1.2 | V p.u. |  | V p.u.
OV2, overvoltage must trip duration | 0.167 | s |  | s
OV1, overvoltage must trip magnitude per unit value | 1.1 | V p.u. |  | V p.u.
OV1, overvoltage must trip duration | 2 | s |  | s
UV1, undervoltage must trip magnitude per unit value | 0.8 | V p.u. |  | V p.u.
UV1, undervoltage must trip duration | 2.25 | s |  | s
UV2, undervoltage must trip magnitude per unit value | 0.45 | V p.u. |  | V p.u.
UV2, undervoltage must trip duration | 1 | s |  | s
OF2, over-frequency must trip magnitude | 62 | Hz |  | Hz
OF2 , over-frequency must trip duration | 1 | s |  | s
OF1, over-frequency must trip magnitude | 61.2 | Hz |  | Hz
OF1 , over-frequency must trip duration | 300 | s |  | s
UF1, under-frequency must trip magnitude | 58 | Hz |  | Hz
UF1, under-frequency must trip duration | 300 | s |  | s
UF2, under-frequency must trip magnitude | 57 | Hz |  | Hz
UF2, under-frequency must trip duration | 1 | s |  | s